## Inputs
LCOH Model — Inputs (edit yellow cells only)
Parameter | Value | Unit | Source / note
Electric boiler efficiency | 0.98 | - | LBNL/DOE tipsheet range 0.95-0.99
Gas boiler efficiency | 0.85 | - | Conventional non-condensing, 0.80-0.90
Electricity price | 0.065 | $/kWh | PLACEHOLDER - update from EIA EPM Table 5.6.A (TX industrial)
Natural gas price | 3.5 | $/MMBtu | PLACEHOLDER - update from EIA TX industrial NG series
Gas boiler capex (installed) | 50000 | $ per MMBtu/hr | Scaled from NREL EFS example; +-50% sensitivity
Electric boiler capex (installed) | 30000 | $ per MMBtu/hr | NREL EFS: electric ~40% below gas; +-50%
Fixed O&M, electric | 0.01 | fraction capex/yr | Common assumption ~1%/yr
Fixed O&M, gas | 0.02 | fraction capex/yr | Burner/tube maintenance heavier than electric
Real discount rate | 0.08 | - | Doc baseline 8% (range 5-12%)
Lifetime | 20 | years | Zuberi et al. 20 yr private perspective
Operating hours | 6000 | hr/yr | LBNL tipsheet 6000; DOE avg CF 47% ~ 4100
Gas CO2 factor | 53.06 | kgCO2/MMBtu fuel | EPA GHG Emission Factors Hub
Grid carbon intensity | 0.365 | tCO2/MWh | eGRID ERCOT average - update annually
kWh per MMBtu | 293.07 | kWh/MMBtu | NREL EFS standard conversion
Legend: yellow = editable input. All other sheets are formulas.

## Model
LCOH per MMBtu delivered — all cells are formulas
Line item ($/MMBtu) | Gas boiler | Electric boiler
Fuel / energy | 4.1176 | 19.4383
Levelized capex | 0.84877 | 0.50926
Fixed O&M | 0.16667 | 0.05
LCOH total | 5.1331 | 19.9976
Cost gap (elec - gas) | 14.8645
Break-even electricity price, full LCOH ($/kWh) | 0.015294
Break-even electricity price, fuel-only ($/kWh) | 0.013769
Spark ratio threshold Pe/Pg (kWh-basis parity) | 13.4235
Emissions (kgCO2 / MMBtu delivered)
Gas boiler | 62.4235
Electric boiler (avg grid CI) | 109.1536
Grid CI parity point (tCO2/MWh) | 0.20874

## Sensitivity
Break-even electricity price (cents/kWh, full LCOH) vs gas price and operating hours
Grid of formulas — recalculates from Inputs. Rows: gas price $/MMBtu; Cols: hours/yr.
Pg \ hours | 4000 | 5000 | 6000 | 7000 | 8000
2 | 1.0156 | 0.96985 | 0.93934 | 0.91755 | 0.90121
3 | 1.409 | 1.3633 | 1.3327 | 1.311 | 1.2946
3.5 | 1.6057 | 1.56 | 1.5294 | 1.5077 | 1.4913
4 | 1.8024 | 1.7567 | 1.7261 | 1.7044 | 1.688
5 | 2.1958 | 2.1501 | 2.1195 | 2.0978 | 2.0814
6 | 2.5892 | 2.5435 | 2.5129 | 2.4912 | 2.4748
7 | 2.9826 | 2.9369 | 2.9063 | 2.8846 | 2.8682
8 | 3.376 | 3.3303 | 3.2998 | 3.278 | 3.2616
Read: if TX industrial retail electricity (Inputs!B6) is above the cell value, gas wins on cost.